## Executive Summary
Review Metrics Summary
Metric | Count
Total Comments Extracted | 73
Approved Status | 0
Rejected Status | 0
Pending Status | 73
Flagged Status | 0

## Electrical Engineering
Standard Input Field |  | Auto Read by Program | Standard Input Field |  | Auto Read by Program
1 | 2 | 3 | 4 | 6 | 7 | 8 | 9 | 10
User Input | User Input | User Input | User Input | User Input | Drawing # from Title Block | Drawing # from Title Block | Drawing Commentary | Classify Error based on Error Description
Date | Contract # | Plant Name | E-Pod WO # | UCC-I Designer | Drawing # | Drawing Title | Errors Description | Category of Error

## GPD
Standard Input Field |  | Auto Read by Program | Standard Input Field |  | Auto Read by Program
1 | 2 | 3 | 4 | 6 | 7 | 8 | 9 | 10
User Input | User Input | User Input | User Input | User Input | Drawing # from Title Block | Drawing # from Title Block | Drawing Commentary | Classify Error based on Error Description
Date | Contract # | Plant Name | E-Pod WO # | UCC-I Designer | Drawing # | Drawing Title | Errors Description | Category of Error

## Pipe Support Engineering
Standard Input Field |  | Auto Read by Program | Standard Input Field |  | Auto Read by Program
1 | 2 | 3 | 4 | 6 | 7 | 8 | 9 | 10
User Input | User Input | User Input | User Input | User Input | Drawing # from Title Block | Drawing # from Title Block | Drawing Commentary | Classify Error based on Error Description
Date | Contract # | Plant Name | E-Pod WO # | UCC-I Designer | Drawing # | Drawing Title | Errors Description | Category of Error

## Piping Engineering
Standard Input Field |  | Auto Read by Program | Standard Input Field |  | Auto Read by Program
1 | 2 | 3 | 4 | 6 | 7 | 8 | 9 | 10
User Input | User Input | User Input | User Input | User Input | Drawing # from Title Block | Drawing # from Title Block | Drawing Commentary | Classify Error based on Error Description
Date | Contract # | Plant Name | E-Pod WO # | UCC-I Designer | Drawing # | Drawing Title | Errors Description | Category of Error

## Plakon
Standard Input Field |  | Auto Read by Program | Standard Input Field |  | Auto Read by Program
1 | 2 | 3 | 4 | 6 | 7 | 8 | 9 | 10
User Input | User Input | User Input | User Input | User Input | Drawing # from Title Block | Drawing # from Title Block | Drawing Commentary | Classify Error based on Error Description
Date | Contract # | Plant Name | E-Pod WO # | UCC-I Designer | Drawing # | Drawing Title | Errors Description | Category of Error

## Structural & Physical Design
Standard Input Field |  | Auto Read by Program | Standard Input Field |  | Auto Read by Program
1 | 2 | 3 | 4 | 6 | 7 | 8 | 9 | 10
User Input | User Input | User Input | User Input | User Input | Drawing # from Title Block | Drawing # from Title Block | Drawing Commentary | Classify Error based on Error Description
Date | Contract # | Plant Name | E-Pod WO # | UCC-I Designer | Drawing # | Drawing Title | Errors Description | Category of Error

## System Engineering
Standard Input Field |  | Auto Read by Program | Standard Input Field |  | Auto Read by Program
1 | 2 | 3 | 4 | 6 | 7 | 8 | 9 | 10
User Input | User Input | User Input | User Input | User Input | Drawing # from Title Block | Drawing # from Title Block | Drawing Commentary | Classify Error based on Error Description
Date | Contract # | Plant Name | E-Pod WO # | UCC-I Designer | Drawing # | Drawing Title | Errors Description | Category of Error

## Unassigned
Standard Input Field |  | Auto Read by Program | Standard Input Field |  | Auto Read by Program
1 | 2 | 3 | 4 | 6 | 7 | 8 | 9 | 10
User Input | User Input | User Input | User Input | User Input | Drawing # from Title Block | Drawing # from Title Block | Drawing Commentary | Classify Error based on Error Description
Date | Contract # | Plant Name | E-Pod WO # | UCC-I Designer | Drawing # | Drawing Title | Errors Description | Category of Error
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | CHECK LENGTHS, ROUND TO 40' INCREMENT -JDM ENSURE QUANTITY HAS ENOUGH LENGTH BASED ON CUT LENGTHS -JDM | Dimension
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | CHECK LENGTHS, ROUND TO 40' INCREMENT -JDM ENSURE QUANTITY HAS ENOUGH LENGTH BASED ON CUT LENGTHS -JDM | Dimension
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | IS THE NUVALOY SUPPOSED TO BE COATED? GEN NOTES SAYS NO -JDM | Notes
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | WE SHOULD LOCATE THIS THRU STEEL AS WELL JCM | Technical
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | WHERE IS THE 0,0 MOVEMENT LOCATION? SHOULD BE A GRID LOCATION JCM | Technical
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | HOPPERS SHOULD BE LOCATED JCM | Technical
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | WHAT IS THIS TO? JCM | Technical
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | CONFIRM IF S12-04 SUFFIX IS ACCEPTABLE ON NUVALOY -JDM | Technical
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | NO GASKET REQUIRED? -JDM DO THESE HOSES CONFIRM IF S12-04 SUFFIX IS ACCEPTABLE ON NUVALOY -JDM 54718-31-C003-08 | Technical
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | NEED ALL OF THESE DRAWINGS ADDED TO THE GEN NOTES PAGE -JDM | Notes
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | DIFFERENT "D" NUMBERS? JCM NO GASKET REQUIRED? -JDM ? EXP -BEK DO THESE HOSES ALSO REQUIRE BUY AMERICAN? IT IS NOT MENTIONED ON THE SPEC DRAWING -JDM S07-00 IS FOR S07-00 IS FOR HARDWARE -JDM 54718-31-C003-08 1" | Technical
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | 1 1/8" IS THIS LOCATED EAST WEST? JCM | Technical
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | NEED TO SHOW GAS FLOW JCM | Technical
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | 1 1/8" CAN THIS TEXT BE ROTATED 180° -JDM SIMILAR LOCATION AS OTHERS EASIER TO FOLLOW JCM | Technical
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | GENERAL COMMENT: NEED TO INDICATE 1 1/2" INSULATION BY OTHERS. - MWR | Technical
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | S07-00 IS FOR HARDWARE -JDM | Technical
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | DO THESE HOSES ALSO REQUIRE BUY AMERICAN? IT IS NOT MENTIONED ON THE SPEC DRAWING -JDM | Technical
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | 176351-080-1-1-S07-00 | Technical
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | 176351-080-1-1-S07-00 54718-31-C002-10-168 54718-31-C002-10-144 54718-31-C002-08-156 54718-31-C002-08-120 54718-31-C002-08-144 54718-31-C002-10-120 C 54718 20 D02 | Technical
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | JCM | Technical
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | JCM THIS IS NOT THE NEST LOCATION FOR THIS NOTE MAYBE ON THE SECTION JCM | Notes
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | N J ? EXP | Technical
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | LATER LATER | Technical
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | TO AIR LINE SEE DRAWING 87W430-4 (C-54718-31-003) | Technical
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | THIS IS NOT THE NEST LOCATION FOR THIS NOTE MAYBE ON THE SECTION JCM | Notes
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | E -BEK | Technical
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | SAME JCM | Technical
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | 10" 150#FLG HOS XX" X 8" X 8" INT 12" X 8" ADAPTO | Technical
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | GENERAL COMMENT: PIPE SUPPORT TAG LOWER BOX SHOULD SHOW "NF". | Technical
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | C-54718-20-D02 LATER 41529-S07-00 | Technical
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | CAN THIS TEXT BE ROTATED 180° -JDM | Technical
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | 08-8"-PC10A-14-017-HC CL EL 337'-2" | Drafting
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | S07-00 IS FOR HARDWARE NOT FITTINGS -JDM | Technical
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | S07-00 IS FOR HARDWARE NOT FITTINGS -JDM | Technical
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | S12-04-P086 | Technical
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | ? EXP -BEK 7/16" | Technical
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | ? 7/16" | Technical
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | (COLD) (HOT) CL EL 345'-11 3/4" TYPICAL FOR HOPPER ROWS | Drafting
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | E -BEK | Technical
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | (COLD) (HOT) CL EL 345'-11 3/4" | Drafting
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | TOO MANY LINES BREAKING IT JUST MAKES IT A BIT HARDER TO FOLLOW | Technical
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | TYPICAL FOR HOPPER ROWS | Technical
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | X" EXP CL ESP UNIT 8 | Drafting
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | S TH DO THESE HOSES ALSO REQUIRE BUY AMERICAN? IT IS NOT MENTIONED ON THE SPEC DRAWING -JDM | Technical
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | SPELLING THIS SHOULD SHOW THE DIFFERENT TYPE OF ASSEMBLIES AND LOOK WHICH ONE NEEDS TO BE INSTALLED WHERE THIS SHOULD BE MORE THAN 1 LINE NUMBER JCM | Cosmetic
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | DO WE TYPICALLY PUT THIS INFORMATION ON OUR BOM? -JDM | BOM
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | LINE NUMBERS ARE NOT MATCHING P&ID VERIFY ALL LINE NUMBERS JCM | Technical
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | 1-7/8" | Technical
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | 3/8" | Technical
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | 3/8" | Technical
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | 1 1/8" | Technical
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | TO AIR LINE SEE DRAWING 87W430-4 (C-54718-31-003) 5 | Technical
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | EXP -BEK | Technical
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | ? EXP -BEK 7/16" | Technical
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | E 7/16" | Technical
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | WHY NOT A SECTION WHERE THE AIRLINE BELONGS JCM | Technical
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | ? EXP -BEK THIS IS NOT CORRECT LOOK AT P&ID VERIFY ALL TAGS JCM 1" | Technical
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | NUVA FEEDEER TAGS ARE CORRECT IF AND ONLY IF SYSTEMS DEPARTMENT REVISES P&ID M-009 TO SWITCH THE EAST AND WEST DUCT LABELS -JDM | Technical
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | EXP -BEK 1" | Technical
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | NEED HOT AND COLD POSITIONS JCM | Technical
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | 1. FOR GENERAL NO (C-54718-31-002). 2. BILL OF MATERIA | Notes
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | C-54718-31-007 -JDM 17? -BEK | Technical
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | NEED TO MAKE SURE WE ARE SPECIFYING WHAT FEEDER IS INSTALLED WHERE SINCE THE FEEDERS ARE NOT TYPICAL FOR ALL JCM Update views - type and location has been updated. Typ all drawings. JJD | Technical
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | -JDM 17? -BEK | Technical
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | WE SHOULD REFERENCE UNIT 1 AND 4 DRAWINGS THIS SHOULD BE A SIMILAR ARRANGEMENT JCM | Technical
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | 017? -JDM | Technical
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | ARE THERE NOT COLUMN GRIDS IN BOTH DIRECTIONS? SIMILAR TO UNIT 1 & 4 -JDM | Technical
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | 001 | Technical
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | 001 | Technical
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | PLE 5 | Technical
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | ARE THERE MULTIPLE SCANS? THE GEN NOTES PAGE SAYS 06/19/25 -JDM 5 6 | Notes
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | Update views - type and location has been updated. Typ all drawings. JJD | Technical
2026-09-13 | CTR-2026-01 | Austin Substation | WO-440192 | Lead Reviewer | C-54718-31-007_A_ | Engineering Review Drawing | C-54718-31-007 | Technical